## Bldg 1 Equipment
Northgate Mill Properties LLC — Building 1, 240 Ferry Street, Easthampton MA 01027 — 22 residential units (1902 brick mill, converted 2006). Equipment schedule as of 2026-09-30.
Asset ID | Location | Equipment Type | Manufacturer | Model | Serial | Install Year | Last Service | Next Due | Status | Notes
B1-BLR-01 | Basement mechanical room | Gas-fired hot water boiler (cast iron sectional) | Calderon Thermal | CT-HW 750 | CT750-06-41182 | 2006 | 2026-08-24 | 2027-08-24 | OK | Annual combustion test 2026-08-24: 83.1% steady state, CO 41 ppm. Lead boiler on the outdoor-reset sequence.
B1-BLR-02 | Basement mechanical room | Gas-fired hot water boiler (cast iron sectional) | Calderon Thermal | CT-HW 750 | CT750-06-41205 | 2006 | 2026-08-24 | 2027-08-24 | OK | Lag boiler. Combustion 82.4%, CO 46 ppm. Low-water cutoff tested and flushed.
B1-CTL-01 | Basement mechanical room | Boiler lead/lag + outdoor reset control | Verity Controls | VX-220 | VX220-14-0771 | 2014 | 2026-08-24 | 2027-08-24 | OK | Reset curve 180F at 0F OA / 140F at 60F OA. Rotates lead weekly.
B1-P-01 | Basement mechanical room | Primary circulator, boiler loop | Stonebridge Pump Works | SB-1400 3HP | SB1400-06-2291 | 2006 | 2026-08-24 | 2027-02-24 | OK | Coupler and seal inspected, no weep. Amp draw 8.1A against 9.4A FLA.
B1-P-02 | Basement mechanical room | Primary circulator, boiler loop | Stonebridge Pump Works | SB-1400 3HP | SB1400-06-2294 | 2006 | 2026-08-24 | 2027-02-24 | Monitor | Mechanical seal weeping approx. 6 drops/min, drip pan staged under flange. SB-1400 casting discontinued 2021 and no rebuild kit is stocked in the northeast; a failure means a full pump-and-flange swap, not a seal. Price a Stonebridge SB-1500 changeout at the next budget cycle.
B1-P-03 | Basement mechanical room | Secondary circulator, north riser | Stonebridge Pump Works | SB-900 1.5HP | SB900-13-8817 | 2013 | 2026-08-24 | 2027-02-24 | OK | Variable speed, running 68% on the DP setpoint.
B1-P-04 | Basement mechanical room | Secondary circulator, south riser | Stonebridge Pump Works | SB-900 1.5HP | SB900-13-8820 | 2013 | 2026-08-24 | 2027-02-24 | OK | Variable speed, running 71% on the DP setpoint.
B1-P-05 | Basement mechanical room | Domestic hot water recirculation pump | Stonebridge Pump Works | SB-310 bronze | SB310-19-4402 | 2019 | 2026-06-11 | 2027-06-11 | OK | Bronze body, on aquastat and timeclock. Balanced 2026-06-11.
B1-WH-01 | Basement mechanical room | Indirect-fired water heater, 119 gal | Castellan Water Systems | CW-119 IND | CW119-11-6034 | 2011 | 2026-06-11 | 2027-06-11 | Monitor | Anode rod pulled 2026-06-11 and found 70% consumed; replaced. Tank is 15 years old against a 15-20 year expectancy and the jacket shows surface rust at the lower head. No leak. Re-inspect the anode at 12 months rather than 24, and carry a replacement in the 2028 capital plan.
B1-ET-01 | Basement mechanical room | Bladder expansion tank, 80 gal | Halden Hydronics | HX-80 | HX80-06-1157 | 2006 | 2026-08-24 | 2027-08-24 | OK | Charged to 12 psi against 12 psi fill. Bladder integrity checked at the Schrader, no water.
B1-BFP-01 | Basement mechanical room, domestic entry | Reduced pressure zone backflow preventer, 2 in. | Castellan Water Systems | CW-RPZ 200 | RPZ200-06-3319 | 2006 | 2026-05-14 | 2027-05-14 | OK | Annual test 2026-05-14, passed. Certificate filed with Easthampton DPW; test tag on device. Next state-required test due 2027-05-14.
B1-BFP-02 | Basement mechanical room, boiler fill | Dual check valve backflow preventer, 3/4 in. | Castellan Water Systems | CW-DC 075 | DC075-06-3324 | 2006 | 2026-05-14 | 2027-05-14 | OK | Tested with the RPZ, passed. Serves the glycol-free boiler makeup.
B1-MAU-01 | Roof, north bay | Gas-fired makeup air unit, 4,000 CFM | NorthPeak Air | NP-MAU 40G | MAU40-08-7712 | 2008 | 2026-09-09 | 2027-03-09 | Monitor | Serves the corridor pressurization. Burner modulates but the flame safeguard has locked out three times since 2025-11, cleared each time by a manual reset with no fault found. NorthPeak no longer supplies the original control board and the aftermarket retrofit is a 6-8 week lead. Log every lockout; plan the control retrofit before the 2027-28 heating season.
B1-SS-01 | Lobby / entry vestibule | Ductless split system, 12 MBH | Meridian Coil | MC-DS12 | DS12-17-2208 | 2017 | 2026-05-02 | 2027-05-02 | OK | Cooling only in practice; heat is on the hydronic loop. Coil washed, 41F delta-T.
B1-SS-02 | Community room, 1st floor | Ductless split system, 18 MBH | Meridian Coil | MC-DS18 | DS18-17-2231 | 2017 | 2026-05-02 | 2027-05-02 | OK | Filters replaced. Condensate pump tested, float clean.
B1-SS-03 | Management office, 1st floor | Ductless split system, 9 MBH | Meridian Coil | MC-DS09 | DS09-17-2244 | 2017 | 2026-05-02 | 2027-05-02 | OK | Charge verified at 8F subcool. No issues reported by Rosa at Loomis Block.
B1-SS-04 | Elevator machine room | Ductless split system, 12 MBH | Meridian Coil | MC-DS12 | DS12-20-5561 | 2020 | 2026-05-02 | 2027-05-02 | OK | Runs year round on a 78F setpoint per the elevator contractor's requirement.
B1-EF-01 | Roof, north bay | Centrifugal roof exhaust fan, corridor | Amberton Fan Co. | AF-RE 180 | RE180-06-9903 | 2006 | 2026-09-09 | 2027-09-09 | OK | Belt and sheave replaced 2026-09-09. Bearings greased, no play.
B1-EF-02 | Roof, south bay | Centrifugal roof exhaust fan, trash room | Amberton Fan Co. | AF-RE 120 | RE120-06-9911 | 2006 | 2026-09-09 | 2027-03-09 | Replace | Audible bearing rumble at startup and 0.9 in. of shaft play at the wheel. The AF-RE 120 frame was dropped by Amberton in 2018 and neither the motor mount nor the wheel is available; the housing would have to be re-cut for any current fan. Quoted as part of J-2604. Trash room odor complaints from units 204 and 206 trace to this fan.
B1-EF-03 | Roof, center bay | Inline exhaust fan, basement mechanical room | Amberton Fan Co. | AF-IL 60 | IL60-15-3372 | 2015 | 2026-09-09 | 2027-09-09 | OK | Interlocked with the boiler call for combustion air. Damper proves.
B1-EF-04 | Basement | Inline exhaust fan, laundry room | Amberton Fan Co. | AF-IL 40 | IL40-15-3380 | 2015 | 2026-09-09 | 2027-09-09 | OK | Lint screen cleaned. Duct run inspected to the exterior louver.
B1-GS-01 | Exterior, west wall | Gas pressure regulator and meter set, 2 in. | Calderon Thermal | CT-REG 200 | REG200-06-0448 | 2006 | 2026-08-24 | 2027-08-24 | OK | 2 psi to the mechanical room, regulated to 7 in. w.c. at the boiler train. Leak-checked.
Legend and source notes
Status: OK = in service, no action. Monitor = serviceable, tracked at a shortened interval. Replace = plan a changeout.
Last Service / Next Due are Mill River Mechanical service visits. RPZ backflow devices are tested annually as required by the Town of Easthampton DPW.
Serial numbers are transcribed from the nameplate at the visit shown in Last Service; where a nameplate was illegible the asset carries the install-year job number instead.
Install Year for pre-conversion equipment is the manufacture year, not the conversion date.
Maintained by Mill River Mechanical Co. LLC, 112 Pleasant Street, Easthampton MA 01027.
Building 1 converted 2006; the hydronic plant and most roof equipment date from that conversion and are now at 20 years.