## Bldg 2 Equipment
Northgate Mill Properties LLC — Building 2, 246 Ferry Street, Easthampton MA 01027 — 19 residential units (1908 brick mill, converted 2019). Equipment schedule as of 2026-09-30.
Asset ID | Location | Equipment Type | Manufacturer | Model | Serial | Install Year | Last Service | Next Due | Status | Notes
B2-BLR-01 | Basement mechanical room | Gas-fired hot water boiler (cast iron sectional) | Halden Hydronics | HB-1000 A | HB1000-98-02214 | 1998 | 2026-08-25 | 2027-02-25 | Replace | Original 1998 plant, retained at the 2019 conversion because it was still firing and the budget went to the units. Combustion test 2026-08-25: 71.4% steady state, CO 188 ppm, stack 512F -- down from 74.9% in 2024. Section 3 shows a dry seep at the push nipple and the rear section is scaled. Halden stopped casting HB-1000 sections in 2016 and the last aftermarket supply is quoted as end-of-life in 2027. It is the sole heat source for 19 units, with no redundancy, through a New England winter. Replacement with a two-boiler condensing plant priced at $86,000 (quote J-2617, 2026-09-18) -- includes venting, near-boiler piping, primary/secondary conversion and controls. Recommend award before 2026-11-15 to install ahead of the heating season.
B2-CTL-01 | Basement mechanical room | Boiler control, single-stage with outdoor reset | Verity Controls | VX-110 | VX110-19-4402 | 2019 | 2026-08-25 | 2027-08-25 | Monitor | Fitted at the 2019 conversion to the 1998 boiler. Single-stage only, so it cannot sequence a two-boiler plant; it will be replaced as part of the B2-BLR-01 changeout and should not be counted as salvage.
B2-P-01 | Basement mechanical room | Primary circulator, boiler loop | Stonebridge Pump Works | SB-1200 2HP | SB1200-19-6618 | 2019 | 2026-08-25 | 2027-02-25 | OK | Amp draw 5.8A against 6.9A FLA. Seal dry.
B2-P-02 | Basement mechanical room | Secondary circulator, east riser | Stonebridge Pump Works | SB-900 1.5HP | SB900-19-6640 | 2019 | 2026-08-25 | 2027-02-25 | OK | Variable speed, 64% on the DP setpoint.
B2-P-03 | Basement mechanical room | Secondary circulator, west riser | Stonebridge Pump Works | SB-900 1.5HP | SB900-19-6643 | 2019 | 2026-08-25 | 2027-02-25 | OK | Variable speed, 66% on the DP setpoint.
B2-P-04 | Basement mechanical room | Domestic hot water recirculation pump | Stonebridge Pump Works | SB-310 bronze | SB310-19-6702 | 2019 | 2026-06-12 | 2027-06-12 | OK | On aquastat and timeclock, 120F return setpoint.
B2-WH-01 | Basement mechanical room | Indirect-fired water heater, 119 gal | Castellan Water Systems | CW-119 IND | CW119-19-8810 | 2019 | 2026-06-12 | 2027-06-12 | OK | Anode 25% consumed at the 2026 pull. Tank fed off B2-BLR-01; the replacement plant keeps this tank and re-pipes the indirect zone.
B2-ET-01 | Basement mechanical room | Bladder expansion tank, 60 gal | Halden Hydronics | HX-60 | HX60-19-2288 | 2019 | 2026-08-25 | 2027-08-25 | OK | Charged to 12 psi. Bladder intact.
B2-BFP-01 | Basement mechanical room, domestic entry | Reduced pressure zone backflow preventer, 2 in. | Castellan Water Systems | CW-RPZ 200 | RPZ200-19-5540 | 2019 | 2026-05-14 | 2027-05-14 | OK | Annual test 2026-05-14, passed. Certificate filed with Easthampton DPW.
B2-BFP-02 | Basement mechanical room, boiler fill | Dual check valve backflow preventer, 3/4 in. | Castellan Water Systems | CW-DC 075 | DC075-19-5548 | 2019 | 2026-05-14 | 2027-05-14 | OK | Tested with the RPZ, passed.
B2-MAU-01 | Roof, east bay | Gas-fired makeup air unit, 3,000 CFM | NorthPeak Air | NP-MAU 30G | MAU30-19-8814 | 2019 | 2026-09-10 | 2027-03-10 | OK | Corridor pressurization. Modulating burner, no lockouts logged since install.
B2-SS-01 | Lobby | Ductless split system, 12 MBH | Meridian Coil | MC-DS12 | DS12-19-7701 | 2019 | 2026-05-03 | 2027-05-03 | OK | Coil washed, 39F delta-T.
B2-SS-02 | Community room, 1st floor | Ductless split system, 18 MBH | Meridian Coil | MC-DS18 | DS18-19-7714 | 2019 | 2026-05-03 | 2027-05-03 | OK | Filters replaced, condensate line flushed.
B2-SS-03 | Fitness room, ground floor | Ductless split system, 24 MBH | Meridian Coil | MC-DS24 | DS24-19-7726 | 2019 | 2026-05-03 | 2027-05-03 | OK | Heaviest runtime unit in the building. Charge verified at 9F subcool.
B2-SS-04 | Package / mail room | Ductless split system, 9 MBH | Meridian Coil | MC-DS09 | DS09-21-3318 | 2021 | 2026-05-03 | 2027-05-03 | OK | Added 2021 after the mail room was enclosed. Under manufacturer warranty to 2031.
B2-EF-01 | Roof, east bay | Centrifugal roof exhaust fan, corridor | Amberton Fan Co. | AF-RE 150 | RE150-19-1120 | 2019 | 2026-09-10 | 2027-09-10 | OK | Direct drive, ECM. No belt. Bearings quiet.
B2-EF-02 | Roof, west bay | Centrifugal roof exhaust fan, trash room | Amberton Fan Co. | AF-RE 120E | RE120E-19-1134 | 2019 | 2026-09-10 | 2027-09-10 | OK | ECM replacement frame for the AF-RE 120. Runs continuous.
B2-EF-03 | Basement | Inline exhaust fan, mechanical room combustion air | Amberton Fan Co. | AF-IL 60 | IL60-19-1152 | 2019 | 2026-09-10 | 2027-09-10 | Monitor | Interlocked to the boiler call. Motorized damper is slow to prove on a cold start, adding 20-40 seconds to the boiler light-off. Serviceable as is, but the interlock and damper are inside the J-2617 replacement scope and should be re-commissioned with the new plant rather than repaired twice.
B2-EF-04 | Ground floor | Inline exhaust fan, fitness room | Amberton Fan Co. | AF-IL 40 | IL40-19-1160 | 2019 | 2026-09-10 | 2027-09-10 | OK | Runs on an occupancy sensor with a 15 minute off delay.
B2-GS-01 | Exterior, east wall | Gas pressure regulator and meter set, 2 in. | Calderon Thermal | CT-REG 200 | REG200-19-0771 | 2019 | 2026-08-25 | 2027-08-25 | OK | 2 psi service. Leak-checked 2026-08-25. Sized to carry the proposed two-boiler plant without a service upgrade.
Legend and source notes
Status: OK = in service, no action. Monitor = serviceable, tracked at a shortened interval. Replace = plan a changeout.
Last Service / Next Due are Mill River Mechanical service visits. RPZ backflow devices are tested annually as required by the Town of Easthampton DPW.
Serial numbers are transcribed from the nameplate at the visit shown in Last Service; where a nameplate was illegible the asset carries the install-year job number instead.
Install Year for pre-conversion equipment is the manufacture year, not the conversion date.
Maintained by Mill River Mechanical Co. LLC, 112 Pleasant Street, Easthampton MA 01027.
Building 2 converted 2019. All equipment is from that conversion except B2-BLR-01, the original 1998 boiler, which was retained.
B2-BLR-01 replacement is quoted at $86,000 under job J-2617 dated 2026-09-18. That quote is the basis for the pipeline opportunity; this schedule is its supporting condition evidence.